## Cover page
Supply and Installation of the 3no. Generators, shelter repairs, and user training for Mpumudde HCIV, Rwesande HCIV and Buwenge GH

## Generator supply-3HFs
Supply and install 3No generators at Mpumudde HCIV, Buwenge General Hospital and Rwesande HCIV and train users on the operational maintenance of the generators supplied (Busoga and Rwenzori)
Bill 1: Preliminaries
Item | Description | Unit | Qty | Unit price excl. VAT (€) | Total price excl. VAT (€)
A | Protection of Works from weather | SUM | 1 |  | 0
B | Tools, plant and false works | SUM | 1 |  | 0
C | Site Supervision | SUM | 1 |  | 0
D | Water for the Works | SUM | 1 |  | 0
E | Temporary light and Power for the Works | SUM | 1 |  | 0
F | Site Security | SUM | 1 |  | 0
G | Hoarding around construction sites, where required | SUM | 1 |  | 0
H | Removing rubbish and reinstating site | SUM | 1 |  | 0
I | Protection of Public and Private Services | SUM | 1 |  | 0
J | Photographs and site records | SUM | 1 |  | 0
K | Workmen compesation policy | SUM | 1 |  | 0
Total Bill 1 excl. VAT (€): |  |  |  |  | 0
Bill 2: Generator Supply |  |  | BOQ Quantity
N° | Description | Unit | Qty | Unit price excl. VAT (€) | Total price excl. VAT (€)
1 | Procurement for supply, installation, and commissioning of 1No 60kVA/48kW, 3 phase, Diesel Generator for Buwenge General Hospital Jinja District, train users on the operational maintenance of the generator supplied. (Busoga). The generator should have remote monitoring enabled up to the end of DLP and Data should be provided monthly or as requested by the client. The generator's exhaust pipe should be extended at least 1.5m above the shelter's roof (See additional specifications under electro-mechanicals). The supplier will be expected to have built-in the generator cost at least three(3) service intervals during the DLP and use the service routines as training opportunities for user refresher training | No. | 1 |  | 0
2 | Ditto in (1) above but 45kVA/36kW for Mpumudde HCIV-Jinja District (Busoga) | No. | 1 |  | 0
3 | Ditto in (1) above but 33kVA/26.4kW for Rwesande HCIV-Kasese District (Rwenzori) | No. | 1 |  | 0
Total Bill 2 excl. VAT (€): |  |  |  |  | 0
Bill 3: Installation and accessory works
N° | Description | Unit | Qty | Unit price excl. VAT (€) | Total price excl. VAT (€)
Installations
Cable installation shall include laying warning tape and provision of cable mark stone at every change of direction along the cable installed length
1 | Supply and install 35mm2 armoured main supply copper cable from power control room to the generator including terminating to board made in Uganda or equivalent. | M | 260 |  | 0
2 | Supply and installation three phase 100A manual changeover switch | No | 1 |  | 0
3 | Provide and install earthing to the generator comprising of Earth electrodes made from Hard drawn copper or copper weld 2mm diameter by 1200mm in two length screwed together complete with cap, earth clamp, manhole and all accessories inclusive testing and test certificate for less than 10 Ohms. | Item | 1 |  | 0
4 | Installation assorted accessories and labour | Item | 1 |  | 0
5 | Supply and install 16mm2 4 core armoured copper cable from existing power control room (Genset) to the multi-purpose hall including terminating to board made in Uganda or equivalent. | M | 100 |  | 0
6 | Excavate trench for 16mm2 cable not exceeding 1.5m and average width of 300mm from existing Generator house to Multi-purpose hall | M | 200 |  | 0
7 | Ditto but for 35mm2 cable to new Generator location near feeder pillar No.1 | M | 130 |  | 0
8 | Weather proof Feeder Pillar: 500A TPN 4way, complete with 500A TPN Incomer MCCB;1Nox400A, 3Nox63A, TPN outgoing MCCBs complete with Voltmeter, Ammeters and all accessories as SCHNEIDER ELECTRIC BLOCK SET manufacture or as made by Electrical Controls and Switchgear or equal approved to be located near power house. | No | 1 |  | 0
9 | Cutting and re-instatement for builders work in concrete, masonry at generator houses and veranda and storm drainage points along cable paths. | Item | 1 |  | 0
Total Bill 3 excl. VAT (€): |  |  |  |  | 0
Bill 4: Shelter minor repairs for Generators
Item | Description | Unit | Qty | Unit price excl. VAT (€) | Total price excl. VAT (€)
BILL 4: SHELTER APPROX 3.5X2.5M
Existing shelters at Mpumudde HCIV, Buwenge GH and Rwesande HCIV to be improved and used as shelters for the new generators see pictures
A | General repairs works to surfaces; walls, floors, aprons, roof as directed by the engineer | Item | 1 |  | 0
PREPARE SURFACE AND APPLY ETCHING PRIMER; apply one coat primer, one undercoat and two Gloss finishing coats; on metal work : to
B | General steel and wooden fascia surfaces | Item | 1 |  | 0
ROOF COVERING
A | Supply and install DCP 9kg fire extinguisher | No | 2 |  | 0
B | Allow for supply and installation of all necessary safety and user signage | Item | 1 |  | 0
C | CARRYOUT MINOR REPAIRS, PREPARE SURFACE AND APPLY ETCHING PRIMER; apply one coat primer, one undercoat, and two roof paint finishing coats; on existing iron sheets surfaces | Item | 1 |  | 0
STEEL GRILLLLED DOORS/VENTS; SEE ELECTROMECHANICAL SPECIFICATION FOR PICTURES OF EXISTING SHELTERS;
D | CARRYOUT MINOR REPAIRS, PREPARE SURFACE AND APPLY ETCHING PRIMER; apply one coat primer, one undercoat and two Gloss finishing coats; on metal work surfaces | Item | 1 |  | 0
E | General door surfaces | Item | 1 |  | 0
Total Bill 4 excl. VAT (€): |  |  |  |  | 0
Bill 5 | Provision of 1/2 day user training on site (in Mpumudde HCIV, Buwenge General Hospital, and Rwesande HCIV including producing soft copy and well bound training manuals. (Busoga and Rwenzori) exc. VAT (€):
Bill 6 | Delivery costs to 3No. Health Facilities exc. VAT (€):
3no generators system and delivery
Bill | Description |  | Total price excl. VAT (€)
1 | Total carried to summary preliminaries: |  | 0
2 | Total carried to summary 3no. Generators, delivery, installation and user training : Mpumudde HCIV, Rwesande HCIV and Buwenge GH |  | 0
6 | Delivery costs to Mpumudde HCIV, Rwesande HCIVs and Buwenge GH : |  | 0
Total 1 - bill carried to main summary for 3no generators system and delivery |  |  | 0
Bill | Description |  | Total price excl. VAT (€)
3 | Total carried to summary Installation and accessory works: |  | 0
4 | Total carried to summary shelter: |  | 0
5 | Provision of 1/2 day user training in a Heath facility: |  | 0
Total 1 - bill carried to main summary 1no. Installation, shelter repairs and user training: |  |  | 0
Total 2 - bill carried to main summary for 3no. Installation, shelter repairs and user training: |  |  | 0
Total 3 - bill carried to main summary for the supply of 3no. Generators, 3no. Installation, shelter repairs, and user training: |  |  | 0
Add 5% contingencies: |  |  | 0
Grand Total for the supply of 3no. Generators, 3no. Installation, shelter repairs, and user training for Mpumudde HCIV, Rwesande HCIV, and Buwenge GH) |  |  | 0